## Sheet1
Cause & Effect Matrix |  | Outputs
Process Input
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
Legend
New HA XNX w/ internal relays for PLC control
existing LEL transmitter
existing toxic transmitter

## Sample
SAMPLE Cause and Effect Matrix Company Name:
Outputs
Process Input | Tag Number | Setpoint | Yellow Strobe | Red Strobe | Alarm Horn | Individual Pilot Lights | Aux. Vent Fan
Normal |  | N/A | OFF | OFF | OFF | OFF | ON
O2 Deficiency #1 | 132-AIT-1935 | 19.5% | ON | OFF | OFF | ON | ON
|  | HI ALARM 16% | OFF | ON | ON | ON | ON
H2S Sensor High | 132-AIT-1934 | 10 PPM | ON | OFF | OFF | ON | ON
|  | HI ALARM 20 PPM | OFF | ON | ON | ON | ON
High LEL (Ceiling) | 132-AIT-1932 | 10% | ON | OFF | OFF | ON | ON
|  | HI ALARM 20% | OFF | ON | ON | ON | ON
High LEL (Floor) | 132-AIT-1933 | 10% | ON | OFF | OFF | ON | ON
|  | HI ALARM 20% | OFF | ON | ON | ON | ON
High CO | 132-AIT-1936 | 35 PPM | ON | OFF | OFF | ON | ON
|  | 50 PPM | OFF | ON | ON | ON | ON
HVAC Low Flow | 132-FSL-1939 | N/A | OFF | OFF | OFF | ON | ON
Temperature Sensor | 132-TSL-1940 | 100° F | ON | OFF | OFF | ON | OFF
|  | HI ALARM 115° F | OFF | ON | ON | ON | OFF
Pressure Sensor | 132-TSL-1941 | 50 PSIG | ON | OFF | ON | ON | OFF
|  | HI ALARM 60 PSIG | OFF | ON | ON | ON | OFF
Emergency Evac Switch | 132-PSL-1937 | N/A | ON | ON | ON | ON | ON
Eye Wash Station | 132-UA-1943 | N/A | ON | ON | ON | ON | ON